## IO LIST
Tag | Device | DI / DO | What it tells the PLC / What the PLC does | Signal Type
PB-Start | Start Pushbutton | DI | Operator wants to start the process. PLC reads this signal. | 24 VDC discrete
PB_Stop | Stop Pushbutton | DI | Operator wants to stop the process. PLC reads this signal. | 24 VDC discrete
LSL-101 | Low-Level Switch | DI | Tank level has reached the LOW point. PLC uses this to decide when to start filling (Auto mode). | 24 VDC discrete
LSH-101 | High-Level Switch | DI | Tank level has reached the HIGH point. PLC uses this to stop filling and prevent overflow. | 24 VDC discrete
HS-101 | Auto/Manual Selector Switch | DI | Tells the PLC which operating mode the operator has selected (Auto or Manual). | 24 VDC discrete
XV-101 | Inlet Solenoid Valve | DO | PLC energizes/de-energizes the valve to open or close the water inlet. | 24 VDC discrete
XL-101 | Tank Full Indicator Lamp | DO | PLC turns this lamp ON when the tank is considered full (or based on your logic). | 24 VDC discrete
XA-101 | Alarm Indicator Lamp | DO | PLC turns this lamp ON whenever an alarm condition exists (overflow, fault, etc.). | 24 VDC discrete | INPUT = information entering PLC | OUTPUT = command leaving PLC
PB_EStop | Emergency Stop Pushbutton | DI | Tells the PLC that the emergency stop has been activated | 24 VDC discrete | Sensor / switch / button → PLC | PLC → actuator / lamp / valve

## PLC_Tags
PLC Tag | Data Type | Description
PB_Start | BOOL | Start pushbutton
PB_Stop | BOOL | Stop pushbutton
PB_EStop | BOOL | Emergency stop pushbutton
LSL_101 | BOOL | Low-level switch
LSH_101 | BOOL | High-level switch
HS_Auto | BOOL | Auto/Manual selector
XV_101 | BOOL | Inlet solenoid valve
XL_Full | BOOL | Tank Full indicator lamp

## Control_Philosophy
A | B
Project | T-101 Automatic Tank Filling System
Document | Control Philosophy
System | Tank T-101
Revision | Rev 0
1. SYSTEM OVERVIEW
The T-101 Automatic Tank Filling System is designed to control the filling of water into Tank T-101. Water enters the tank through inlet solenoid valve XV-101. Tank level is monitored using low-level switch LSL-101 and high-level switch LSH-101. The system can be operated in Automatic or Manual mode using selector switch HS-101. The PLC uses Fill_Request as the internal command for the filling operation. When Fill_Request is active and the emergency stop is not active, XV-101 is energized to allow filling.
2. OPERATING MODES
2.1 Automatic Mode | 2.2 Manual Mode
In Automatic mode, filling shall begin when the Low-Level Switch (LSL-101) is activated. The PLC shall set Fill_Request, causing XV-101 to open. | In Manual mode, the operator may initiate filling by pressing PB-START. Fill_Request shall remain active after the Start pushbutton is released.
Filling shall continue until the High-Level Switch (LSH-101) is activated. The PLC shall then reset Fill_Request, causing XV-101 to close and XL-Full to turn ON. | Filling shall stop when PB-STOP is pressed or when LSH-101 is activated.
3. EMERGENCY STOP
When the Emergency Stop is activated:
Fill_Request shall be reset.
XV-101 shall close.
XA-Alarm shall turn ON.
After the Emergency Stop is released, the system shall not automatically restart. A new Start command is required.
4. FILLING TIMEOUT
Purpose: Prevent continuous filling if the tank does not reach the High-Level Switch within the permitted filling time.
1. The filling timer shall run while XV-101 is open and LSH-101 is not activated.
2. If LSH-101 activates before the timer reaches 30 seconds, filling shall stop normally and the timer shall reset.
3. If the timer reaches 30 seconds:
Fill_Timeout shall become TRUE.
Fill_Request shall be reset.
XV-101 shall close.
XA-Alarm shall turn ON.

## Cause_Effect
Cause (Input / Event) | Effect (PLC Action)
PB-START pressed (Manual Mode) | Set Fill_Request → Open XV-101
PB-STOP pressed | Reset Fill_Request → Close XV-101
LSL-101 activated (Auto Mode) | Set Fill_Request → Open XV-101
LSH-101 activated | Reset Fill_Request → Close XV-101 → Turn XL-Full ON
E-Stop activated | Reset Fill_Request → Close XV-101 → Turn XA-Alarm ON

## Test_results
Test | Expected | Actual | Result
Manual start | Valve opens | Valve opened | PASS
Manual latch | Valve remains open after Start release | Yes | PASS
Manual stop | Valve closes | Valve closed | PASS
Auto start | Valve opens when LSL-101 is active | Valve opened | PASS
High level | Valve closes and Full indication turns ON | Correct | PASS
E-stop | Valve closes and alarm turns ON | Valve closed and alarm turned ON | PASS
Timeout | Valve closes and alarm turns ON | Timeout occurred and alarm turned ON | PASS